{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["浙江医药2025年消防器材需求清单"],"read":"whole","date_system":"1900"}

{"sheet":"浙江医药2025年消防器材需求清单","index":0,"n_rows":51,"n_cols":10,"rows_kept":51,"merged":[[0,0,0,9],[2,3,3,3],[2,4,3,4],[2,5,3,5],[7,3,8,3],[9,3,13,3],[9,4,13,4],[9,5,13,5],[14,3,16,3],[14,4,16,4],[17,3,21,3],[17,4,21,4],[17,5,25,5],[22,3,23,3],[22,4,23,4],[24,3,26,3],[24,4,25,4],[28,3,29,3],[28,4,29,4],[30,4,32,4],[31,3,32,3],[33,3,40,3],[33,4,40,4],[35,5,36,5],[37,5,38,5],[44,3,46,3],[44,4,46,4],[44,5,46,5],[47,4,48,4],[47,5,48,5],[50,0,50,9]]}
["浙江医药2025年度消防器需求清单"]
["序号","产品名称","规格","执行标准","技术要求","品牌\n（符合下述之一即可）","单位","预估\n数量","单价\n(元)","金额\n(元)"]
[1,"聚氨酯衬里消防水带(白)","13型，65mm，25米","GB 6246-2011《消防水带》","军用接口；扎口铁丝不少于555道，使用胶带保护，加装橡胶保护套，橡胶垫圈安装牢固；卡扣位置铅丝需要做好防锈处理以防锈蚀；长度准确，出厂信息清晰；消防器材S标张贴到位，流向准确。","芜湖中安消防设备有限公司\n九江消防装备有限公司\n泰州市神龙消防科技有限公司\n黄山消防水带厂","盘",500]
[2,"聚氨酯衬里消防水带(白)","13型，80mm，20米",{"$nulls":3},"盘",30]
[3,"内扣式接扣","KD65","GB 12514.1-2005 《消防接口 第1部分：消防接口通用技术条件》","军用型；接扣表面光滑，无毛刺、气孔；接扣卡簧稳固，不易脱扣；橡胶圈安装牢固；消防器材S标张贴到位，流向准确。","芜湖中安消防设备有限公司\n九江消防装备有限公司\n泰州市神龙消防科技有限公司","付",500]
[4,"直流水枪","QZ3.5/5","GB 8181-2005 《消防水枪》","军用型；水枪表面光滑，无毛刺、气孔；接头底座安装紧固到位；橡胶圈安装牢固；消防器材S标张贴到位，流向准确。","芜湖中安消防设备有限公司\n九江消防装备有限公司\n泰州市神龙消防科技有限公司\n江山市江升消防器材有限公司\n高邮腾达消防科技有限公司","支",200]
[5,"直流-喷雾水枪","/","GB 8181-2005 《消防水枪》","军用型；水枪表面光滑，无毛刺、气孔；直流-喷雾切换能力顺畅，关闭时完全，不漏水；接头底座安装紧固到位；橡胶圈安装牢固；消防器材S标张贴到位，流向准确。","芜湖中安消防设备有限公司\n九江消防装备有限公司\n泰州市神龙消防科技有限公司\n江山市江升消防器材有限公司\n高邮腾达消防科技有限公司","支",100]
[6,"置地型灭火器箱","XMDF5-2","XF 139-2009 《灭火器箱》","厚度标准不小于1.2mm；灭火器箱提手处有防割伤保护；连接合页开启顺畅，焊接到位；消防器材S标张贴到位，流向准确。","杭州利江消防器材有限公司\n余姚市众安消防器材有限公司\n永康市牛安消防器材厂","只",50]
[7,"304不锈钢灭火器箱","XMDF5-2",null,"厚度标准不小于1.2mm；304不锈钢材质；灭火器箱提手处有防割伤保护；连接合页开启顺畅，焊接到位；消防器材S标张贴到位，流向准确。","杭州市发达消防器材有限公司\n河南瑞宸消防器材有限公司","只",300]
[8,"手提式干粉灭火器","MFZ/ABC2","GB 4351-2023《手提式灭火器》\n（2025年1月1日实施）","压力表压力显示绿色区域；消防器材S标张贴到位，流向准确。","浙江欧伦泰防火设备有限公司","只",10]
[9,"手提式干粉灭火器","MFZ/ABC5",{"$nulls":3},"只",3000]
[10,"手提式干粉灭火器","MFZ/ABC4\nMFZ/ABC4-I",{"$nulls":3},"只",2000]
[11,"手提式干粉灭火器","MF/ABC8",{"$nulls":3},"只",20]
[12,"手提式水基型灭火器","3L",{"$nulls":3},"只",200]
[13,"金属钠专用灭火器","8kg","GB 4351-2023《手提式灭火器》\n（2025年1月1日生效）\nXF 979-2012  《D类干粉灭火剂》","压力表压力显示绿色区域；消防器材S标张贴到位，流向准确。","浙江宇安消防装备有限公司","只",5]
[14,"金属镁专用灭火器","8kg",null,null,"浙江宇安消防装备有限公司\n浙安集团有限公司","只",5]
[15,"金属灭火器","MFZ/D4",null,null,"浙江浙安消防设备有限公司","只",10]
[16,"手提式CO2灭火器","MT/2","GB 4351-2023《手提式灭火器》\n（2025年1月1日实施）\n","消防器材S标张贴到位，流向准确。","浙江欧伦泰防火设备有限公司","只",10]
[17,"手提式CO2灭火器","MT/2-I",{"$nulls":3},"只",10]
[18,"手提式CO2灭火器","MT/3",{"$nulls":3},"只",60]
[19,"手提式CO2灭火器","MT/5",{"$nulls":3},"只",160]
[20,"手提式CO2灭火器","MT/7",{"$nulls":3},"只",20]
[21,"悬挂式干粉灭火器","6kg","XF 602-2013《干粉灭火装置》","压力表压力显示绿色区域；消防器材S标张贴到位，流向准确。",null,"只",200]
[22,"悬挂式七氟丙烷灭火器","8kg",{"$nulls":3},"只",10]
[23,"推车式干粉灭火器","MFT/ABC20","GB 8109-2023 《推车式灭火器》\n（2025年1月1日实施）","压力表压力显示绿色区域；消防器材S标张贴到位，流向准确。",null,"辆",10]
[24,"推车式干粉灭火器","MFT/ABC35",{"$nulls":3},"辆",10]
[25,"移动式泡沫灭火推车","PY4-200L",null,null,"江苏共安消防设备有限公司","辆",3]
[26,"移动式泡沫灭火推车","PY4-500L",{"$nulls":3},"辆",2]
[27,"泡沫比例混合器","PHFA","GB 20031-2024《泡沫灭火系统及部件通用技术条件》\n（2025年6月1日实施）",null,"上海万安达明信消防系统有限公司\n河南省威特消防设备有限公司","只",5]
[28,"泡沫发生器","PCL4/PCL6",null,null,"永康市永安消防器材有限公司\n河南省威特消防设备有限公司","只",2]
[29,"室内消火栓","SWN65","GB 3445-2018《室内消火栓》","栓口尺寸满足军用消防接扣安装要求；消防器材S标张贴到位，流向准确","永康市永安消防器材有限公司\n乐清市宏达消防设备制造有限公司","个",150]
[30,"室外消火栓","SS100/65-1.6","GB 4452-2011《室外消火栓》",null,"乐清市宏达消防设备制造有限公司","个",50]
[31,"室外消火栓扳手","普通型38cm",null,null,"乐清市宏达消防设备制造有限公司","个",50]
[32,"室外消火栓箱","80*65*24","GB14561-2019《消火栓箱》\n（2020年4月1日实施）","厚度不小于1.2mm；开启角度不小于120°；玻璃尺寸根据分批订单另行要求。","杭州市发达消防器材有限公司\n浙江浙安消防设备有限公司\n余姚市众安消防器材有限公司","只",5]
[33,"室内消火栓箱","160*70*24",null,null,"杭州市发达消防器材有限公司\n浙江浙安消防设备有限公司\n永康市牛安消防器材厂","只",20]
[34,"室外消火栓箱门框","80*65",null,null,"杭州市发达消防器材有限公司\n余姚市众安消防器材有限公司","只",5]
[35,"室内消火栓箱门框","160*70",{"$nulls":3},"只",40]
[36,"304不锈钢室外消火栓箱","80*65*24",null,null,"杭州市发达消防器材有限公司\n河南瑞宸消防器材有限公司","只",80]
[37,"304不锈钢室内消火栓箱","160*70*24",{"$nulls":3},"只",50]
[38,"304不锈钢室外消火栓箱门框","80*65",null,null,"杭州市发达消防器材有限公司\n河南瑞宸消防器材有限公司\n余姚市众安消防器材有限公司","只",30]
[39,"304不锈钢室内消火栓箱门框","160*70",null,null,"杭州市发达消防器材有限公司\n河南瑞宸消防器材有限公司","只",10]
[40,"灭火毯","1500*1500","XF 1205-2014  《灭火毯》",null,"江西穗华玻纤有限公司","条",5]
[41,"消防水泵接合器","SQS100-1.6型","GB 3446-2013 《消防水泵接合器》",null,"乐清市宏达消防器材厂","只",5]
[42,"抗溶性水成膜泡沫","3%AFFFAR/6%S/AR","符合GB15308-2006《泡沫灭火剂》","配套资料齐全，提供废旧泡沫液回收服务。","江苏锁龙科技有限公司\n江苏共安消防设备有限公司\n宁波能林消防器材有限公司","kg",12000]
[43,"泡沫枪","PQ8","符合GB25202-2010《泡沫枪》","304不锈钢材质","芜湖中安消防设备有限公司\n九江消防装备有限公司\n浙江金盾消防器材有限公司\n高邮市沐氏消防装备有限公司\n章丘市济南消防设备有限公司","只",5]
[44,"泡沫枪","PQ4",{"$nulls":3},"只",2]
[45,"泡沫枪","QP8/0.7Z",{"$nulls":3},"只",2]
[46,"MFZ/ABC干粉灭火剂","充装","GB 4066-2017  《干粉灭火剂》","原厂充装","浙江欧伦泰防火设备有限公司","kg",2000]
[47,"MT/CO2灭火剂","充装","GB 4396-2024《二氧化碳灭火剂》\n2025年12月1日实施",null,null,"kg",1500]
[48,"合计"]
["注：1、供货时间：供方接订单后原则上要求3-15天内到货（实际到货如不能满足需求，双方再行协商）；其中序号12-23项：部分存在接订单后要求当天到货的应急情况。\n    2、对序号12-23、40项：要求所供产品为下订单当月最新产品（实际供货过程，如有偏差，双方再行协商）。"]